## Sheet1
Room by room ventilation heat loss calculation following EN 12831-1:2017 standard calculation method

External temperature			-2

Room name			Livingroom	Hall	Kitchen	Bed 1	Bed 2	Bed 3	Landing	Bathroom	Totals
Room internal temperature		C	21	18	18	18	18	18	18	22		C
Room volume		m3	56.93	15.84	17.28	23.52	20.74	9.5	19.01	19.01	181.83	m3
Envelope of the room		m2	36.72	9.6	20.16	13.88	14.88	8.28	7.92	21.6	133.04	m2
Design air volume flow of the ATDs in the ventilation room (I)	qv,ATD,design,i	m3/hr	0	0	10	0	0	0	0	10	20	m3/hr
Effective air change rate		ACH	0.49	0.46	1.04	0.45	0.55	0.66	0.32	1.01		ACH
Effective air change rate		ACH	0.98	0.92	2.09	0.90	1.09	1.32	0.63	2.01		ACH

Effective air volume flow		m3/hr	27.9	7.3	18.0	10.5	11.3	6.3	6.0	19.1	106.5	0.59	ACH
Effective air volume flow		m3/hr	55.8	14.6	36.1	21.1	22.6	12.6	12.0	38.3	213.1	1.17	ACH

6.3.3.3.1 Ventilation heat loss of the building (build) / zone (z) / room (I)

6.3.3.3.1 Building (15)					756	W

6.3.3.3.1 Zone (16)		W	212	48	119	70	75	42	40	152	756	W

Max value of the following is selected:	qv,leak+ATD,i + qv.open.i	m3/h	28	7	18	11	11	6	6	19
	fi,z*qv.min.i – qv.techn.i		14.23	3.96	4.32	5.88	5.19	2.38	0.00	4.75

6.3.3.3.1 Heated space (17)		W	424	96	238	139	149	83	79	303	1512	W
Density x specific heat	p.cp		0.33	0.33	0.33	0.33	0.33	0.33	0.33	0.33
Internal temperature	O.int.i	C	21	18	18	18	18	18	18	22		C
Outside temperature	O.e	C	-2	-2	-2	-2	-2	-2	-2	-2		C
Rec temperature	O.rec.z	C	0	0	0	0	0	0	0	0		C
Transfer temperature	O.transfer.ij	C	0	0	0	0	0	0	0	0		C
	qv.env.i	m3/h	55.8	14.6	36.1	21.1	22.6	12.6	12.0	38.3		m3/h
	qv.open.i	m3/h	0	0	0	0	0	0	0	0		m3/h
	qv.min.i	m3/h	28.465	7.92	8.64	11.76	10.37	4.75	0	9.505		m3/h
	n.min.i		0.5	0.5	0.5	0.5	0.5	0.5	0	0.5
	qv.techn.i	m3/h	0	0	0	0	0	0	0	0		m3/h
	qv.sup.i	m3/h	0	0	0	0	0	0	0	0	0	m3/h
	qv.transfer.ij	m3/h	0	0	0	0	0	0	0	0	0	m3/h
	qv.exh.i		0	0	0	0	0	0	0	0	0	m3/h
	qv.comb.i		0	0	0	0	0	0	0	0	0	m3/h

6.3.3.3.2 External air volume flow into the room (I) through the building envelope	qv,env,i	m3/hr	55.8	14.6	36.1	21.1	22.6	12.6	12.0	38.3		m3/hr
Air volume flow through additional infiltration into the zone (z)	qv,inf-add,z		107	107	107	107	107	107	107	107
External air volume flow into the ventilation zone (z) through the building envelope	qv,env,z		107	107	107	107	107	107	107	107
External air volume flow into the zone (z) through large openings	qv.open.z		0	0	0	0	0	0	0	0
External air volume flow into the room (I) through leakages and ATDs in accordance with Formula (19)	qv,leak+ATD,i		27.9	7.3	18.0	10.5	11.3	6.3	6.0	19.1
Orientation factor (default: 2, B.2.14)	fdir,z		2	2	2	2	2	2	2	2
External air volume flow into the room (I) through large openings	qv,open,i		0	0	0	0	0	0	0	0	0	m3/h

Formula 19 (page 35)	qv,leak+ATD,i	m3/hr	27.9	7.3	18.0	10.5	11.3	6.3	6.0	19.1	107	m3/hr
External air volume flow into the ventilation zone (z) through leakages in accordance with (20)	qv.leak.z	m3/h	101	101	101	101	101	101	101	101		m3/h
Envelope of the room (I)	A.env.i	m2	36.72	9.6	20.16	13.88	14.88	8.28	7.92	21.6		m2
Envelope of the ventilation zone (z)	A.env.z	m2	133.04	133.04	133.04	133.04	133.04	133.04	133.04	133.04		m2
External air volume flow into the zone (z) through ATDs in accordance with Formula (21)	qv.ATD.z		5.43	5.43	5.43	5.43	5.43	5.43	5.43	5.43
Design air volume flow of the ATDs in the ventilation room (I)	qv,ATD,design,i		0	0	10	0	0	0	0	10	20	m3/hr
Design air volume flow of the ATDs in the ventilation zone (z)	qv,ATD,design,z		20	20	20	20	20	20	20	20

Formula 20 (page 36)	qv.leak.z		101
ATD authority of the ATDs in zone (z) in accordance with Formula (22)	a.ATD.z		0.051
External air volume flow into the ventilation zone (z) through the building envelope	qv,env,z		107

Formula 30	qv.ATD.50.z		108.63	m3/hr @ 50 Pa
Design air volume flow of the ATDs in the ventilation zone (z)	qv,ATD,design,z		20
Pressure exponent for leakages, Default value from B.2.14	Vleak_z		0.67

Formula 22 ATD authority of the ATDs in zone (z)	a.ATD.z		0.051
	qv.ATD.50.z		108.63	m3/hr @ 50 Pa
Envelope of the ventilation zone (z)	A.env.z		133.04	m2
Specific air permeability of the envelope at 50pa	qenv50		15.20	m3/h.m2

Formula 21 External air volume flow into the zone (z) through ATDs	qv.ATD.z		5.43
ATD authority of the ATDs in zone (z)	a.ATD.z		0.05
External air volume flow into the ventilation zone (z) through the building envelope	qv,env,z		106.54

6.3.3.3.4 External air volume flow into the ventilation zone (z) through the building envelope (page 37)	qv,env,z	m3/hr	107					m3/hr
Exhaust air volume flow from the ventilation zone (z) (Sum of rooms, I)	qv,exh,z	m3/hr	0					m3/hr
Combustion or any other technically required air volume flow into the ventilation zone (z) (Sum of rooms, I)	qv,comb,z	m3/hr	0					m3/hr
Supply air volume flow into the ventilation zone (z) (Sum of rooms, I)	qv,sup,z	m3/hr	0					m3/hr
Air volume flow through additional infiltration into the ventilation zone (z) in accordance with 6.3.3.3.5	qv,inf-add,z	m3/hr	107					m3/hr

6.3.3.3.5 Air volume flow through additional infiltration into the zone (z) (page 37)	qv,inf-add,z	m3/hr	107					m3/hr
Specific air permeability of the envelope at 50pa	qenv50	m3/h/m2	15.2	Corrected upwards as test noted 240 m2 envelope area					m3/h/m2
Envelope of the ventilation zone (z)	Aenvz	m2	133.04					m2
Air volume flow into the ventilation zone (z) through ATDs at a pressure difference of 50 Pa in accordance with Formula (29)	qvATD.50z		108.63
Volume flow factor	fqv,z		0.05
Adjustment factor taking into account the additional pressure difference due to unbalanced ventilation in accordance with Formula (29)	fe,z		1.00

Formula 29 (fe,z) (page 38)	fe,z		1.00
Adjustment factor for the number of exposed facades	ffac.z		8
Volume flow factor	fqv,z		0.05
Exhaust air volume flow from the ventilation zone (z) (Sum of rooms, I)	qv,exh,z	m3/hr	0					m3/hr
Combustion or any other technically required air volume flow into the ventilation zone (z) (Sum of rooms, I)	qv,comb,z	m3/hr	0					m3/hr
Supply air volume flow into the ventilation zone (z) (Sum of rooms, I)	qv,sup,z	m3/hr	0					m3/hr
Design air volume flow of the ATDs in the ventilation zone (z)	qv,ATD,design,z	m3/hr	20					m3/hr
Specific air permeability of the envelope at 50pa	qenv50	m3/h/m2	15.2					m3/h/m2
Envelope of the ventilation zone (z)	Aenvz	m2	133.04					m2
Air volume flow into the ventilation zone (z) through ATDs at a pressure difference of 50 Pa	qvATD.50z	m3/hr	108.632482527472					m3/hr

## Sheet2
Room volume		58.8	m3
Envelope of the room		54	m2
Effective air change rate		0.78	ACH

6.3.3.3.1 Ventilation heat loss of the building (build) / zone (z) / room (I)

6.3.3.3.1 Heated space (17)		359	W
Density x specific heat	p.cp	0.34
Internal temperature	O.int.i	20	C
Outside temperature	O.e	-3	C
Rec temperature	O.rec.z	0	C
Transfer temperature	O.transfer.ij	0	C
External air volume flow into the room (I) through the building envelope	qv.env.i	45.9	m3/h
	qv.min.i	29.4	m3/h

6.3.3.3.2 External air volume flow into the room (I) through the building envelope	qv,env,i	45.9	m3/hr
External air volume flow into the room (I) through leakages and ATDs in accordance with Formula (19)	qv,leak+ATD,i	23.0
Orientation factor (default: 2, B.2.14)	fdir,z	2

Formula 19 (page 35)	qv,leak.i	23.0	m3/hr
External air volume flow into the ventilation zone (z) through leakages in accordance with (20)	qv.leak.z	91	m3/h
Envelope of the room (I)	A.env.i	54	m2
Envelope of the ventilation zone (z)	A.env.z	214	m2		Envelope cancels out!

Formula 20 (page 36)	qv.leak.z	91
External air volume flow into the ventilation zone (z) through the building envelope	qv,env,z	91

6.3.3.3.4 External air volume flow into the ventilation zone (z) through the building envelope (page 37)	qv,env,z	91	m3/hr
Air volume flow through additional infiltration into the ventilation zone (z) in accordance with 6.3.3.3.5	qv,inf-add,z	91	m3/hr

6.3.3.3.5 Air volume flow through additional infiltration into the zone (z) (page 37)	qv,inf-add,z	91	m3/hr
Specific air permeability of the envelope at 50pa	qenv50	8.5	m3/h/m2		2040
Envelope of the ventilation zone (z)	Aenvz	214	m2		Envelope cancels out!
Volume flow factor	fqv,z	0.05
Adjustment factor taking into account the additional pressure difference due to unbalanced ventilation in accordance with Formula (29)	fe,z	1.00